## External-SA6-2
| City Utilies Design Standards Manual | Exhibit SA6-2 Exterior Grease Interceptor Sizing Tool for Food Service Establishments
Version: July 2026
Flow Rate
* Based on Fixture Volume and two-minute drainaige period
| Flow Rate = | (L x W x D x #compartments)*.75
231 in^3/gal * 2 minutes
Fill in Yellow Highlighted Cells
Sink 1
| Length |  | inches
| Width |  | inches |  | Flow Rate | 0 | GPM
| Depth |  | inches
# compartments
Sink 2
| Length |  | inches
| Width |  | inches |  | Flow Rate | 0 | GPM
| Depth |  | inches
# compartments
Sink 3
| Length |  | inches
| Width |  | inches |  | Flow Rate | 0 | GPM
| Depth |  | inches
# compartments
Sink 4
| Length |  | inches
| Width |  | inches |  | Flow Rate | 0 | GPM
| Depth |  | inches
# compartments
|  |  |  | Total Flow Rate |  | 0 | GPM
Required Grease Storage
Restaurant Type |  | Choose A-F
Low Grease Production |  | A | 0.005 | lbs/meal (no flatware) |  | Sandwich Shop, Convenience Store, Bar, Sushi Bar, Deli, Snack Bar, Frozen Yogurt, Hotel Breakfast Bar
|  | B | 0.0065 | lbs/meal (with flatware)
Moderate Grease Production |  | C | 0.025 | lbs/meal (no flatware) |  | Coffee House, Pizza, Grocery Store (no fryer), Ice Cream Parlor, Fast Food, Greek, Indian, Low Grease Output FSE (w/fryer)
|  | D | 0.0325 | lbs/meal (with flatware)
High Grease Production |  | E | 0.035 | lbs/meal (no flatware) |  | Cafeteria, Family Restaurant, Italian, Steak House, Bakery, Buffet, Chinese, Mexican, BBQ, Sea Food, Fried Chicken, Grocery Store (w/fryer)
|  | F | 0.0455 | lbs/meal (with flatware)
# of Meals Per Day
# of Day per Pump Out Cycle |  |  |  | Min Value of 30; Max value of 90
Minimum Grease Storage Capacity |  |  |  | #N/A | lbs
Minimum Exterior Grease Interceptor Size |  |  |  | #N/A | #N/A
For retrofit buildings and remodels with limited space, flow control devices may be used upstream of an internal grease interceptor to assist in slowing the flow rate and ensure all flow is adequately passing through the grease interceptor. New builds or remodels with ample space will require a grease interceptor sized to meet the calculated flow rate. Any flow control device shall be vented and terminate not less than 6 inches above the flood rim level or higher if required by manufacturer’s instructions. The Engineer shall ensure the flow restriction will not cause sewer backup in the upstream connections.